High Water Alarm System

The High Water Alarm System monitors the lowest elevation inlet in the Mitchell Interchange and is located at the end of Tunnel 1 on the W-N System Ramp.

It is an active monitoring system.  An initial alarm activates as water reaches a preset level within the inlet. A second alarm activates if water ponds above the inlet.

The monitoring system provides alarms via email and phone call to alert MCSO, STOC, and City of Milwaukee Fire Department dispatch in the event of high-water detection. Please note, until one of the agencies acknowledges receiving an alarm, the monitoring system continues to send the alarm every 15 minutes.

MCSO and the City of Milwaukee FD respond using their standard flood management protocols. The STOC responds by notifying the RIMC and monitoring the area for traffic impacts. An email notification should also be sent to the internal notification list.

Tunnel Lighting Alarm System

Key tunnel lighting system components consist of the lights, uninterrupted power supply, back-up generators, and lighting buildings.  A SINS Incident should be created for all alarms received in the control room.

- The tunnel lighting controls are located in the Tunnel Control Buildings. Each Tunnel Control Building contains a monitoring device that provides intrusion and environmental alarms to the STOC Control Room.

- Each tunnel includes a primary and secondary electrical circuit to provide uninterruptable power for emergency egress lighting. If primary electric power is lost, a natural gas fueled emergency generator automatically becomes operational to power emergency egress lights (every fourth tunnel light and the four illuminated tunnel exit signs). When activated, the emergency power circuit alarm alerts the STOC through an e-mail notification.

- If emergency lighting fails, Control Room Operators will receive a “pop-up” message on the workstation computer screens, prompting  them to notify the Milwaukee County Public Works Department.

The tables below provide the responsible agency and contact information for the tunnel lighting system.

Tunnel Lighting Agency Responsibilities and Contact Information